## Total
KARAIKUDI ZONAL OFFICE - INTERIOR FURNISHING, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK ( KARAIKUDI ZONE )
Amount(Rs.)
A | MAIN WORKS
1 | INTERIOR/FURNISHING WORK
2 | ELECTRICAL WORK
3 | DATA CABLING WORK
4 | A/C WORK
TOTAL

## Interior
KARAIKUDI ZONAL OFFICE - INTERIOR FURNISHING, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK ( KARAIKUDI ZONE )
ROUGH COST ESTIMATE AND BILL OF QUANTITIES
S NO | PARTICULARS | QTY | UNIT | RATE(Rs) | AMOUNT (Rs)
1 | PARTITIONS
a | Full Height Blocked Partition
| Providing full height double skin fully blocked partitions using aluminium plain rectangular sections of 2 1/2"x 1 1/2" size spaced at 2'0" c/c maximum for the frame work, fixed with 6mm plywood on both sides and lined with 1mm tk. laminate (Fusion Maple - wood finish) with necessary grooves of 1mm thick. The rate shall include the cost of providing 100mm wide skirting with 1mm tk. laminate (Black) at base and a 100mm wide border (Brown) at the top including making necessary slots for cable conduits to pass through and all incidental materials etc., complete.( Record, dining,strong room,ups room) | 252 | Sft
b | Partly Glazed Partition Manager Cabin:
| Providing full height double skin partly glazed partitions using aluminium sections of 2 1/2"x1 1/2" size spaced at 2'0" c/c maximum for the frame work, fixed with 6mm plywood on both sides and lined with 1mm tk. laminate (Fusion Maple - wood Finish) with necessary grooves of 1mm thick. The rate shall include the cost of providing 100mm wide skirting with 1mm tk. laminate (Black) at base and a 100mm wide border (Brown) at the top and shall include the cost of providing 6mm tk. plain float glass to suitable sizes, including making necessary slots for cable conduits to pass through and all incidental materials etc., complete. | 980.5 | Sft
c | Low Height Partition
| Providing low height double skin partitions along with Counter Divider partition wicket gate of the same type using aluminium sections of 2 1/2" x 1 1/2" size spaced at 2'0" c/c maximum for the frame work, fixed with 6mm plywood on both sides and lined with 1mm tk. laminate (Steem Beech - 278 of Formica India) with necessary grooves of 1mm thick. The rate shall include the cost of providing 100mm wide skirting with 1mm tk. laminate (Black - 301 of Formica India) at base & including making necessary slots for cable conduits to pass through and all incidental materials etc., complete. | 415 | Sft
2 | FRONT COUNTER 12MM GLASS
| Providing front glazing for cash cabin above counter from 3'9" to 7'0" height, and inbetween banking counters using 12mm thick plain glass including edge polishing & etching. | 105 | Sft

## Interior 2
DOORS
a) | ENTRANCE DOOR
| To be made out of 12mm thk glass with etching as per design. The glass with etching has to be fixed with top & sides rails of 2½"x4" and bottom rails of size 2½" x 6". The rails to be made out of beech wood The door shall have 18" long s/s handle (as shown in the drawing ) and also double action floor spring of specified make. The door frame to be mde out of 5"x 2½" best quality beech wood. The etching in glass pattern to be done strictly following instructions of the Architect or following the drawing attached. The exposed wood of frames, rails to be polished as per instructions of the architect. NB: The size of the door may slightly vary as per site conditions for matching the elevation on the fixed glazing. All exposed edges of the glass to be machine polished. The rails are to be made as per the design of the architect. Bank Entrance door (4'0" X 7'0") | 42 | Sft
b) | FLUSH DOORS
i) | Door (3'0" x 7'0") | 1 | No
c) | SEMIGLAZED DOORS
i) | ZM , Azm & Vc cabin Door ( 3'0" x 7'0" ) | 3 | No
ii) | Conference doors (2'6"x 7'0" ) | 2 | No
4 | COUNTERS
Providing and assembling banking counter and single window counter unit as shown in drawing of size not less than 5'0" x 2'6" x 2'6" or as per site requirements, with regular drawer - 1 No. and shelves on one side, a keyboard drawer at centre and a platform for CPU onto other side for each counter as shown in drawing using 19mm thick commerical plywood lined with 1.0mm thick laminate (Fusion Maple - Wood finish) for all the exposed surfaces, including providing skirting 4" wide with 1.0mm thk laminate (Black) on both sides to match with the adjoining partition and 4" wide border at top with 1.0mm thk laminate (Brown).customer top will be at 3 ' 9 " including thickness of the granite ( 19mm Thk ) which will have machine polished edges as shown in the drawing
All the plywood edges shall have teak wood lipping and all inner surfaces shall be painted with two coats of enamel paint over a coat of primer & two coats of putty. The rate shall include providing, fixing & painting a foot rest using first class seasoned country frame of size 3" x 1 1/2".Necessary hardware fittings like draw sliders, hinges, multipurpose locks with set keys, handles shall be provided.
i) | CM | 20 | Rft
ii) | Off | 50 | Rft
iii) | Cl | 16 | Rft

## Interior 3
5 | SERVER ROOM WORKING COUNTER
| Working top will be 2' - 6" ht to be provided as per instructions given by the architect. Rest of the working counter as per specifications in fabricated out of 18mm ply for top, sides and 6mm ply for back. The work station will have drawer units, keyboard tray, cpu platforms, leg rest etc., and drawings attached in tender and specifications.All clarificationss to be taken before quoting the prices and no extra cost shall be entertained at the time of execution.The entire work as per the instruction of the Architect at the time of execution. | 6.75 | Rft
6 | FOLDED DINING TABLE | 13 | Rft
Supplying and fixing of pantry table using 18mm plywood with proper support and finished with matching lamination sheet, the inner surfaces shall be painted.The exposed surfaces shall be pasted with 1mm laminate with necessary grooves as per the drawing.
7 | TABLE
Manufacturing and placing in position of tables for managers & staff using 19mm. thick plywood to size as shown in drawing. One keyboard drawer & three storage drawers for manager tables, and one keyboard drawer at centre, one drawer at right or left side below counter top with storage cupboard below for offier/staff tables, space to accomodate CPU etc., shall be provided. All the plywood edges shall have teak wood lipping & the inner surfaces shall be painted.The exposed surfaces and top shall be pasted with 1mm laminate. Necessary hardware fittings like draw sliders, lock, handles, wire manager etc., shall be provided. A sheet of 10mm thick glass shall be provided over the manager tables only.
a) | Z.Manager Table(6'0"X3'0"X2'6") | 1 | No
b) | A.Z Manager Table(5'0"X3'0"X2'6") | 1 | No
c) | Conference Table(6'0"X3'0"X2'6") | 1 | No
d) | Reception Table(4'0"X2'6"X2'6") | 1 | No
8 | STORAGE
Manufacturing and placing in position of side storage for SWC, officer & clerical staff using 19mm. thick plywood as shown in drawing. All the plywood edges shall have teak wood lipping & the inner surfaces shall be painted.The exposed surfaces shall be pasted with 1mm laminate with necessary grooves as per the drawing. Necessary hardware fittings like draw sliders, lock, handles etc., shall be provided.
i) | Conference Hall | 64.75 | Sft
ii) | ZM | 50.75 | Sft
iii) | AZM | 10 | Sft
iv) | CM Back Side | 80 | Sft
v | Officers | 75 | Sft
vi) | Conference Hall | 42.5 | Sft
vii) | Record & Dining | 168 | Sft
9 | WRITING LEDGE WITH 12mm GLASS TOP
| Made out 18 mm ply as per design and exposed external surfaces to be laminated and internal surface to be painted with top provided 12 mm thk etched glass with machine polished edges . The entire work has to be done to the satisfaction of the architect. The design given has to be strictly followed | 1 | No
10 | cheque drop box/ Complaint
| Providing cheque drop box/ Complaint/ Suggestion 1'6" length, 0'9" wide and 1'6" height with 19mm tk. Plywood and lined with 1mm tk. Laminate(Fusion Maple - Wood finish) for top & exposed sides. Exposed edges of plywood shall be fixed with teak wood beading suitably polished and the back side shall be covered with 6mm tk. plywood. The inner sides shall be painted with two coats of enamel paint over acoat of primer & two coats of putty. | 1 | No
11 | NOTICE BOARD
| Providing and fixing of the soft board on the customer lobby made of jolly board with a fabric of B / R @ 200 / - per meter .The design and the entire work has to be done as per the instructions of the architect a the time of execution | 24 | Sft
12 | Vertical Blinds:
| Providing and fixing 100mm wide Vista Make or equavalent vertical blinds of approved make quality and colour shade and pattern. Rate shall include necessary scotch guard treatment on both side. The overlaps should be uniform and adequate | 284 | Sft
13 | FALSE CEILING ( GYPBOARD )
| Providing & fixing suspended gypboard false ceiling, which includes Providing & fixing G.I perimeter channels of size 27mm, 0.5mm thk having one flange of 20mm & another flange of 20mm along with perimeter of the ceiling, screws fixed to brick wall/partitions with the help of rawl plugs & Screws. Then suspending G.I intermediate channels of size 45mm, 0.9mm thk with two flanges of 15mm each from the soffit at 1200mm centres with stell G.I hanger of width 25mm,0.5mm thk fixed to soffit with G.I. cleat & steel expansion fasteners. Ceiling section of 0.5mm thickness having knurled wedge of 51.5mm and two flanges of 26mm each with leafs of 10.5mm are then fixed to the intermediate channel with the help of connecting clips and in direction perpendicular to the intermediate channel at 450mm centres. 12.5mm tapered edge gypboard is then screwed fixed to ceiling section with 25mm dry wall screws at 230mm centres | 2800 | Sft
with requiste jointing compound, paper tapes, finisher and premier suitable for Gypsum plaster boards. The entire work shall be finished as per instructions of the Architect. And also finished with two or more coats of acrylic emulsion paint of approved shade and make. No extra cost shall be entertained in completing the entire work in all respect.
Total Interior Works
say

## Electrical
, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK
1 | PARTITIONS
a) | FULL HEIGHT BLOCKED PARTITIONS
|  | NO | UNIT | L | B | H | TOTAL
i) | Record Room Entry | 1 | Sft | 28 |  | 10.5 | 294
|  | -2 | Sft | 3 |  | 7 | -42
[5 empty] | TOTAL |  | -252
b) | PARTLY GLAZED PARTITIONS
i) | Video Conference | 1 | Sft | 18.5 |  | 10.5 | 194.25
|  | -1 | Sft | 3 |  | 7 | -21
ii) | Conference Hall | 1 | Sft | 16 |  | 10.5 | 168
|  | -2 | Sft | 2.5 |  | 7.25 | -36.25
iii) | ZM | 1 | Sft | 30 |  | 10.5 | 315
|  | -1 | Sft | 3 |  | 7 | -21
iv) | AZM | 1 | Sft | 22.5 |  | 10.5 | 236.25
|  | -1 | Sft | 3 |  | 7 | -21
v) | Server | 1 | Sft | 13 |  | 10.5 | 136.5
|  | -1 | Sft | 2.5 |  | 7 | -17.5
h) | Entrance | 1 | Sft | 8.5 |  | 10.5 | 89.25
| Entrance Door | -2 | Sft | 3 |  | 7 | -42
[5 empty] | TOTAL |  | -980.5
c) | LOW HEIGHT PARTITIONS
i) | CM - 1 | 3 | Sft | 16.25 |  | 4.5 | 219.375
ii) | CM - 2 | 1 | Sft | 5 |  | 4.5 | 22.5
iii) | CM - 3 | 1 | Sft | 11 |  | 4.5 | 49.5
iv) | Officers | 1 | Sft | 16.5 |  | 4.5 | 74.25
f) | Ups | 1 | Sft | 9.75 |  | 5 | 48.75
[5 empty] | TOTAL |  | -414.375
5 | 12mm GLASS
|  | NO | UNIT | L | B | H | TOTAL
i) | Banking Hall | 1 | Sft | 10 |  | 10.5 | 105
[5 empty] | -637400 |  | -105
3 | DOOR
ENTRANCE DOOR
|  | NO | UNIT | L | B | H | TOTAL
| MD | 2 | Sft | 3 |  | 7 | 42
[5 empty] | TOTAL |  | -42
FLUSH & SEMIGLAZED DOOR
a) | D | 3 | Sft | 3 |  | 7 | 63
b) | D1 | 3 | Sft | 2.5 |  | 7 | 52.5
d) | D2 | 1 | Sft | 3 |  | 7 | 21
[5 empty] | TOTAL |  | -136.5
4 | COUNTERS
|  | NO | UNIT | L | B | H | TOTAL
a) | CM | 4 | Nos | 5 |  | 1 | 20
b) | Off | 10 | Nos | 5 |  | 1 | 50
c) | Cl | 4 | Nos | 4 |  | 1 | 16

## Electrical 1
[5 empty] | TOTAL |  | -86
6 | SERVER ROOM COUNTER
|  | NO | UNIT | L | B | H | TOTAL
| Server | 1 | Rft | 6.75 |  |  | 6.75
[5 empty] | TOTAL |  | -6.75
7 | TABLES
|  | NO | UNIT | L | B | H | TOTAL
| Z.Manager Table(6'0"X3'0"X2'6") | 1 | Nos |  |  |  | -1
| A.Z Manager Table(5'0"X3'0"X2'6") | 1 | Nos |  |  |  | -1
| Conference Table(6'0"X3'0"X2'6") | 1 | Nos |  |  |  | -1
| Reception Table(4'0"X2'6"X2'6") | 1 | Nos |  |  |  | -1
[5 empty] | TOTAL |  | -4
8 | STORAGE CUPBOARD
|  | NO | UNIT | L | B | H | TOTAL
i) | Conference Hall | 1 | Sft | 9.25 |  | 7 | 64.75
ii) | ZM | 1 | Sft | 7.25 |  | 7 | 50.75
iii) | AZM | 1 | Sft | 4 |  | 2.5 | 10
iv) | CM Back Side | 4 | Sft | 8 |  | 2.5 | 80
v) | Officers | 10 | Sft | 3 |  | 2.5 | 75
vi) | Conference Hall | 1 | Sft | 17 |  | 2.5 | 42.5
vii) | Record & Dining | 1 | Sft | 24 |  | 7 | 168
[5 empty] | TOTAL |  | -258.25
9 | WRITING LEDGE WITH CHEQUE DROP BOX
| Banking Hall | 1 |  |  |  |  | -1
10 | NOTICE BOARD
|  | NO | UNIT | L | B | H | TOTAL
| Banking Hall | 2 | Sft | 4 |  | 3 | 24
[5 empty] | TOTAL |  | -24
11 | VERTICAL BLINDS
|  | NO | UNIT | L | B | H | TOTAL
i) | Banking Hall | 1 | Sft | 6.5 |  | 5.5 | 35.75
ii) | Banking Hall | 10 | Sft | 4.5 |  | 5.5 | 247.5
[5 empty] | TOTAL |  | -283.25
12 | GYPSUMBOARD
|  | NO | UNIT | L | B | H | TOTAL
| Server Cabin , Mananger & Hall | 1 | Sft | 2800 |  |  | 2800
[5 empty] | TOTAL |  | -2800

## Electrical cost
KARAIKUDI ZONAL OFFICE - INTERIOR FURNISHING, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK ( KARAIKUDI ZONE )
ROUGH COST ESTIMATE AND BILL OF QUANTITIES
Sl.No | Description Of Work | Unit | Qty | Rate | Amount
A | Supply&Installation&Commisioing of the following Main Panel Board
1 | Supply, erection, testing and commissioning of wall mounting, dust and vermin proof, bus bar chambers shell made of 14/16 SWG CRCA sheet, with powder coating, extendable on either sides MAIN SWITCH consisting of the following: Incomer: 125A MCCB Input - 1 No. 100A bus bar R1 Y1 B1 voltage indication lamps etc. - 1 sets 1 Nos. 0-500V 96 sq.mm analog voltmeter, Ammeter with selector switch and required CT ciols Out Goings: 100A TPN MCCB - 1 No ( A/Cs ) 63A TPN MCCB - 2 Nos. ( UPS, & PDB ) 32A TPN MCCB - 2 Nos. (Lighting and Spare ) | Set | 1
B | Supply&Installation&Commisioing of the following
1 | AC DB (8WAY VTPN DB)
Three Phase, Vertical Distribution board
with nuetral bar,earth bar,cables ties,top and
bottom removable gland plate and with necessary
adopter boxes if any.The DB should be IP 42 metallic
double door with provisioin of MCB etc as
required including cuting of wall and plastering the
same with neat finish.It comprising as flolows:-
Incomer :
100A TPN MCCB -1Nos
Outgoings:
63A TP MCB -3Nos
| 32/25A SP MCBs- 12Nos | Set | 1
2 | LIGHTING DB(6 WAY TPN DB)
Three Phase, Phase Segrigated Distribution board
with nuetral bar,earth bar,cables ties,top and
bottom removable gland plate and with necessary
adopter boxes if any.The DB should be IP 42 metallic
double door with provisioin of MCB etc as
required including cuting of wall and plastering the
same with neat finish.It comprising as flolows:-
Incomer : 40A TPN MCB
Outgoings:
| 10/6A SP MCBs- 12Nos | Set | 1
3 | POWER DB(4WAY TPN DB)
Three Phase, Phase Segrigated Distribution board
with nuetral bar,earth bar,cables ties,top and
bottom removable gland plate and with necessary
adopter boxes if any.The DB should be IP 42 metallic
double door with provisioin of MCB&ELCB etc as
required including cuting of wall and plastering the
same with neat finish.It comprising as flolows:-
Incomer : 63A TPN MCB
Outgoings:
| 32/25/20A SP MCBs- 12Nos | Set | 1
4 | COMPUTER DB(12WAY SPN DB)
12 Way SPN Distribution board
with nuetral bar,earth bar,cables ties,top and
bottom removable gland plate and with necessary
adopter boxes if any.The DB should be IP 42 metallic
double door with provisioin of MCB&ELCB etc as
required including cuting of wall and plastering the
same with neat finish.It comprising as flolows:-
Incomer : 40ADP MCB
Outgoings:
| 10A SP MCBs- 6Nos | Set | 2
5 | Supply&Installation of the following with the necessary
enclosure and adopter boxes if necessary,
| a)63A TPN MCB | Set | 2
| b)63A DP MCB | Set | 2
| c)40A DP MCB | Set | 2
6 | Supply&Installation of 32A Metal Clad Socket with
top in a specified company manufactured box with
| suitable rating MCB for AIR CONDITIONS | set | 12
7 | Providing and fixing 63A automatic phase shifter 3phase in single phase out switch for 5kva UPS. | set | 2
8 | Supply&Installation of 63A 4Pole Change over switch | set | 1
C | LT CABLES
1 | Supply&Laying of the following cables in built up
trenches,on wall, or in the ground as per the case may be,
with proper clamping with necessary fixing materials etc.
Installing testing&commisioing of 1100V grede UG
cable as per IS 7098/1554 ( Finolex/ Universal)
a | 3.5Corex70Sqmm Aluminium Armored cable Main | Mtr | 50
b | 3.5Corex50Sqmm Aluminium Armored cable AC DB | Mtr | 15
c | 3.5Corex35Sqmm Aluminium Armored cable PDB Main | Mtr | 18
d | 3.5Corex25sqmm Aluminium Armored cable LDB | Mtr | 30
2 | End Termination of the above cables with proper Glands
and Lugs
a | 3.5Corex70Sqmm Aluminium Armored cable Main DB | Set | 2
b | 3.5Corex50Sqmm Aluminium Armored cable power DB | Set | 2
c | 3.5Corex35Sqmm Aluminium Armored cable LDB Main | Set | 2
d | 3.5Corex25sqmm Aluminium Armored cable LDB |  | 4
D | WIRING
1 | Light/Fan point wiring with 3 of 1.5 sqmm PVC
insulated copper conductor to be laid in 2mm suitable
PVC conduit with Bend,Couplings, etc.. And fixing with
clamps screws etc.All conduits to be laid above the
false ceiling/partition/concealed in the wall
etc. Wiring to be connected with supply&Fixing of
6A Modular type switch(MK/ROMA) with suitable
Modular plate and metal Box
| a) One light Controlled by One Switch | Pts | 50
| b) Two light Controlled by One Switch | pts | 5
| c) 6A Switch box Sockets in the switch board itself | Pts | 15
| d) Ceiling fan with regulator | Pts | 3
| e) wall bracket fan point (6A socket with 6A switch) | pts | 23
| f) Calling bell point with Calling bell instrument | Pts | 1
2 | Supply&Wiring with Flame Retardant
insulated PVc wire as per grade IS 994
for Circuits,Computer point,Power points within 2mm thk
PVc conduits with necessary accessories and with
proper clamps and to be concealed below the false
ceiling It comprises as follows:-
a) 3Runs of 2.5Sqmmcopper wire in PVC conduit for
| lighting circuit mains | Mtr | 350
b) 3Runs of 2.5Sqmmcopper wire in PVC conduit for
| Power points | Mtr | 400
C) 3Runs of 2.5Sqmm copper wire in PVC conduit for
| computer points | Mtr | 450
d) 2Runs of 4Sqmm copper wire+1.5Sqmm copper
| wire in PVC conduit A/C Wiring | Mtr | 150
e) 2Runs of 6Sqmm copper wire+2.5Sqmm copper
| wire in PVC conduit A/C Wiring | Mtr | 100
f) 4Runs of 10 Sqmm copper wire+2.5Sqmm copper
| wire in PVC conduit UPS MAIN | Mtr | 20
g) 2Runs of 10Sqmm copper wire+2.5Sqmm copper
| wire in PVC conduit UPS OUTPUT MAIN | Mtr | 30
E | POWER POINT OUTLETS
1 | Supply&Installation of 3 Nos of 6A Sockets controlled by
1of 16A Switches with front plate with enclosure and
| other accessories etc..(MK /ROMA) | Set | 22
2 | Supply&Installation of 1Nos of 6A Socket controlled by
1No 6A Switch with front plate with enclosure and other
| accessories etc..(MK /ROMA) | Set | 20
3 | Supply&Installation of 1Nos of 16A Socket controlled by
1No 16A Switch with front plate with enclosure and other
| accessories etc..(MK /ROMA) | set | 5
4 | Supply&Installation of 3 Nos of 16A Sockets controlled by
2of 16A Switches with front plate with enclosure and
| other accessories etc..(MK /ROMA) | Set | 2
F | LIGHTING FIXTURES
1 | Supply, Fixing & Commisioning of Recess mounting type compact vertical Flat Panel 34W LED 2'x2' fitting in Down Rods with white finish and other fixing accessories. | set | 44
2 | Supply, Fixing & Commisioning of Recess mounting type compact vertical round shaped 18 W LED downlighter fitting with white finish and other fixing accessories., | set | 23
3 | Supply&Fixing of Patti Type LED 20Watts Fiitings | Set | 8
4 | Supply&Fixing exhaust fan | set | 3
5 | Supply&Fixing & Commisioning of wall mounting fan
with necessary Down Rods and with all
| fixing accessories., | Set | 23
6 | Supply&Fixing & Commisioning of 48" ceiling fan
with necessary Down Rods and with all
| fixing accessories., | Set | 3
7 | Supply and fixing 10w LED Lamp for Toilet | Set | 2
G | EARTHING
1 | Providing dedicated earthing with 600x600x3.15
mm copper plate along with 50mm dia.10feet
long G.I pipe with other accessories in the earth
filled with necessary salt,charcoal,etc. It should
be covered with G.I Manhole cover with necessary
| civil works.etc.. | Set | 1
2 | Supply & Laying of 10 Sqmm PVC Insulated Multi
strand copper conductor laid in 25mm dia PVC pipe for
Dedicated earth leads from the earth electrodes to
| the UPSsystem | Mtr | 60
3 | Providing general earthing with 50mm dia.10feet
long G.I pipe with other accessories in the earth
filled with necessary salt,charcoal,etc. It should
be covered with G.I Manhole cover with necessary
| civil works.etc.. | Set | 1
4 | Supply&Laying of 8SWG copper wire | Mtr | 100
F | TELECOMMUNICATION
1 | Supply&Laying of 2 Pair Telephone Cable within PVC
| Conduit and its necessary accessories etc.. | Mtr | 650
2 | Supply&Laying of 20Pair Telephone Cable within PVC
| Conduit and its necessary accessories etc.. | Mtr | 50
3 | Supply&Installation of RJ II Jack with necessary Face
| plate and Box for connecting telephone points | Set | 20
4 | Supply & fixing of 20 pair KRONE Box with lock and key | Set | 2
TOTAL

## Data 1
KARAIKUDI ZONAL OFFICE - INTERIOR FURNISHING, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK ( KARAIKUDI ZONE )
S.No | Description Of Work | Unit | Qty | Rate | Amount
DATA CABLING
1 | Supply&Laying of CAT 6 Data Communication cable in 2mm
thk heavy duty 20mm dia PVC conduit and makinng holes in
| the aluminium partitions/wall all accessories as required (DLink) | Mtr | 675
2 | Supply&Installation,Testing&Commisioing of Modular type
1Nos of RJ45 Female Jack housed in GI anodised metal box
with suitable Faceplate fixing the same in the wall/partitions
| with all accessories etc. as required. | Set | 24
3 | Supply and fixing of 1M Mounting Cord | Set | 24
4 | Supply and fixing of 2M Mounting Cord | Set | 24
5 | Supply&Installation of 24por cat6 SWITCH | Set | 1
6 | Supply&Installation of 16por cat6 SWITCH | Set | 1
7 | Supply and installation of 24port cat 6 jack panel | Set | 2
8 | Supply and installation of 9u wall mounting rack | Set | 1
TOTAL

## Data 2
KARAIKUDI ZONAL OFFICE - INTERIOR FURNISHING, ELECTRICAL, DATA CABLING AND AIR CONDITIONING WORKS FOR INDIAN BANK ( KARAIKUDI ZONE )
ROUGH COST ESTIMATE AND BILL OF QUANTITIES
Sl.No | Description Of Work | Unit | Qty | Rate | Amount
1 | Supply, Installation, Testing and commissioning of
indoor and outdoor split air conditioner with remote
control, with 3 star rating units and necessary civil
works etc., The rate of units is including the supply
and laying of 3 mtr of copper pipes with insulations,
rubbers, white cements etc., (Brand: Voltas)
a | 1 TR - Video conference | 1 | No
b | 1.5 TR - main conference 3Nos, AGM - 1 No | 4 | No
c | 2 TR - ZM- 1 No & Banking Hall - 4 Nos | 5 | No
2 | Supply and laying of copper pipes with rubber
| insulations, rubbers, white cements etc., | 45 | Mtr
3 | Supply and installation of Stabilizer for following
units
a | 1 TR - 2 KVA | 1 | No
| 1.5 TR - 3 KVA | 4 | No
c | 2 TR - 4 KVA | 5 | No
4 | Supply and Installation of Outdoor Stand with
| necessary civil works | 10 | No
5 | Supply and laying of PVC Blue pipes for water
| drain from the indoor units. | 70 | Mtr
6 | Civil works like cutting AC hole,packing,drain pipe cutting and packing with mortar etc. | 1 | Ls
Airconditioning works Total: