## DMS (hidden)
ESTIMATE INTERIOR WORKS FOR INDIAN BANK AT KASNA, GREATER NOIDA BRANCH & ATM.
DETAIL MEASUREMENT SHEET FOR FURNISHING WORK
A | SCHEDULE - 'A' (FURNISHING WORK)
S.NO. | DESCRIPTION | Length (Fts.) | Height (Fts) | numbers | QTY. | QTY.
1 | SUSPENDED FALSE CEILING
1.1 | FALSE CEILING ( GYPSUM BAORD)
1 | BANKING HALL | 1150 | 1 | 1 | 1150
1150
DEDUCTIONS
| GRID FALSE CEILING | 805 | 1 | 1 | 805
805
[5 empty] | 345 | 350
1.2 | FALSE CEILING (24"x24" GRID FALSE CEILING)
| GRID FALSE CEILING | 805 | 1 | 1 | 805
[5 empty] | 805 | 805
2 | PARTITIONS WORK
2.1 | FULL HEIGHT SOLID PARTITION
1 | STRONG ROOM | 12 | 7 | 1 | 84
| BACK AREA ENTRY | 5 | 8.5 | 1 | 42.5
[5 empty] | 126.5 | 130
2.2 | Single skin partition
| BACK AREA ENTRY | 7 | 2 | 1 | 14
[5 empty] | 14 | 14
2.3 | Full Height Glazed partition
1 | MANAGER CABIN | 12 | 8.5 | 1 | 102
| MANAGER CABIN | 9 | 8.5 | 1 | 76.5
| CASH CABIN | 9.25 | 7 | 1 | 64.75
[5 empty] | 243.25 | 250
2.4 | Low. Height Semi Glazed Partition
1 | SWO | 5.5 | 4.5 | 4 | 99
| SWO | 4.5 | 4.5 | 2 | 40.5
| FLAP DOOR | 3.5 | 4 | 1 | 14
[5 empty] | 153.5 | 155
2.5 | Glazed Partition
| CASH | 5 | 2 | 1 | 10
| SWO | 4.5 | 2.5 | 2 | 22.5
| P. OFFICER | 4.5 | 1.5 | 1 | 6.75
[5 empty] | 39.25 | 40
3 | DOOR & ACCESSORIES
3.1 | Main Entrance Door
| MAIN ENTRY | 3.5 | 7 | 1 | 24.5
[5 empty] | 24.5 | 25
3.2 | Main Entrance Fixed Glazing
| FRONT FIXED AREA | 10 | 8.5 | 1 | 85
ABOVE ENTRY
[5 empty] | 85 | 60.5
3.3 | Supplying and fixing of Dorma/GEZE Dline / | 1 | 1 | 2 | 2 | 2
3.4 | Supplying and fixing of mortice door lock of | 1 | 1 | 5 | 5 | 5
3.5 | Supplying and fixing of door stopper SS G | 1 | 1 | 5 | 5 | 5
4 | WORKING COUNTER
4.1 | CASH COUNTER & SINGLE WINDOW | 5 | 1 | 1 | 5 | 5
4.2 | RUNNING COUNTER | 4.5 | 1 | 4 | 18 | 18
5 | TABLE & FURNITURE
TABLES
5.1 | BRANCH MANAGER TABLE - (5'-6" X 2'-6") | 1 | 1 | 1 | 1 | 1
5.2 | RUNING COUNTER & UTILITY TABLE :- Table width is 2'-0" wide and excluding glass on table top. | 5 | 1 | 1 | 5 | 5
6 | STORAGE & SIDE UNIT
6.1 | Side and Back Unit
|  | 3 | 2.5 | 6 | 45 | 45
6.2 | low ht. Storage | 24 | 2.5 | 1 | 60 | 60
6.3 | Main Electrical Panel Cabinet | 4.5 | 8.5 | 1 | 38.25 | 40
7 | OTHER MISCELLANEOUS ITEMS
7.1 | PIN UP / NOTICE BOARD
| the periferi. | 4 | 2 | 3 | 24 | 25
7.2 | PAINTING
|  | 1500 | 1 | 1 | 1500 | 1500
7.3 | WRITING LEDGER & Cheque & sugestion box | 1 | 1 | 1 | 1 | 1
7.4 | Outer Shutter Boxing | 18 | 5 | 1 | 90 | 90
7.5 | ROLLING BLINDS | 4 | 8.5 | 1 | 34 | 35
7.6 | PILLAR & WALL PANELLING
| COLUMN | 5 | 8.5 | 3 | 127.5
[5 empty] | 127.5 | 130

## ELECTRICAL
BLANK B.O.Q OF ELECTRICAL WORK FOR INDIAN BANK AT Pachderwa kalan BRANCH
B | SCHEDULE - 'B' (ELECTRICAL WORK)
SL No | PARTICULARS | UNIT | QTY | RATE | AMT | QTY | RATE | AMT
1 | ELECTRICAL WIRING & EARTHING
1.1 | Supply,laying,connection & testing of light,fan point, wiring by 2x1.5mmsq(2x3/.029) +1x1mmsq PVC insulated, multistrand single core copper conductor FRLS wire maintating the colour code as per direction in PVC conduite of 20mm with ISI mark 1.5mm thickness to conceal in wall partition mending good the damage, complete with PVC circular box, bend to be done as per drawaing including 3 point ceiling rows wherever required GI saddle to be used for fixing,metal flexiable/PVC flexiable pipe may use if requied in partition wall. All PVC pipes should be with ISI mark. No joints will be allowed inside pipe,light, fan & plug point complete with modular type switch plate & MS box . rate Including the main circuite line 2x2.5mmsq+1x1.5mmsq earth PVc insulated Cu. Wire from DB to switch board ,maintaining the colour code. Circuite line for lighting switch board & 6Amps plug board are to be drawn from lighting DB to Lighting board & plug point board (independent ), 6/16 Amps plug point line are to be draw from power DB.as per DBschedule /SLD
a) | 1 light by 1 switch ,UPS Pt 3 In branch | Nos. | 8 | 550 | 4400 | 17
b) | 2 light by 1 switch | Nos. | 19 | 650 | 12350 | 11
e) | Ceiling fan point with step type electronic regulator | No | 4 | 650 | 2600 | 3
f) | Same as above, but for exhaust fan excluding regulator. | No | 3 | 500 | 1500 | 2
g) | Same as above 5A Point in the switchboard itself. (for branch 4 No & ATM 1 No) | No | 6 | 250 | 1500 | 5
h) | same as above Wiring for call-bell point including buzzer | No | 1 | 550 | 550 | 1
i) | Wiring (2x2.5mmsq+1x1.5mmsq from power DBs) for independant 6A multi pin socket at walls along with 6A modular type switches board housed in painted MS box (upto 3 independent plug points can be taken in one circuit). For wall Fan | No | 10 | 450 | 4500 | 7
1.2 | Supply and installation of modular type 2 nos 6A & multi pin sockets with 2 nos 6 Amp one way switch housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer including wiring for Raw power socket outlet using 2 R runs of 2.50 Sqmm and single run of 1.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 20mm PVC conduit to be laid in floor, partitions, etc. complete with all accessories (looping 2 sets of 2x6A socket outlet in one circuit- from DB) (Raw power). for counter ( Each counter 1 Nos +BM :2 Nos, ATM 1No:,Pantry 1No.:) | No | 8 | 600 | 4800 | 5
1.3 | Supply and installation modular type 16A, 5-pin socket with 16A one way switch housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer , the rate shall include wiring fusing 2R 4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories (for line printer : or optional).(upto 2 independent plug points can be taken in one circuit) C.C :1No. BM.;1 No.: Alternative counter 2No + Banking Hall 1 No+ Pantry 1No ,ATM :1No) | Nos. | 5 | 900 | 4500 | 6
1.4 | Supply and installation of power supply disconnection arrangement for strong room consisting of 1 no 10A DP MCB housed in manufacturer's powder coated MS box to be fixed inside the strong room and connected with 1 no 3-pin metal clad plug with 2 metre long 3 core 2.5 sqmm PVC insulated flexible copper conductor cable. | Set | 1 | 2500 | 2500 | 1
1.5 | Acs electrification :-
(a) | Supply and fixing 25 Amps 3-pin modular socket with 25 Amp one way switch with indicator (near AC indoor unit) housed in manufacturers MS powder coated box to be concealed in wall includding Wiring using 2R4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) -(from Stabilzer to IDU)Supply. (2 Nos for ATM), Stablizer to be installed in the panel room. | Nos | 5 | 1500 | 7500 | 4
(b) | Supply and fixing 25 Amp - 3 pin metal clad socket with plug controlled by a 25 Amp SP MCB (for Ac wall mounted stabilizers) housed in manufacturers MS powder coated box to be concealed in wall including Wiring using 2R 4.0 sqmm & single run of 2.5 sqmm PVC insulated multi stranded single core copper conductor FRLS wire in 25mm PVC conduit to be laid in floor, partitions, etc complete with all accessories. (for split AC units) from AC DB to Stablizer (2 Nos for ATM) | Nos | 5 | 1500 | 7500 | 4
2 | LAYING OF CABLE :
2.1 | Supply laying fixing main power with 50mm sq 3.5 core PVC insulated,PVC sheated Alu.Conductor, 1100 v. grade armoured cable complete with 02 nos 8 SWG bear GI.wire as running earth .( Meter panel to Main Panel & Dgset to Main Panel )
|  | Mts. | 15 | 550 | 8250 | 15
2.2 | End termination of 50mmsq 3.5 Core armoured cable,complete with brass cable gland , Alu. Lug, PVC tape.
|  | Nos | 4 | 150 | 600 | 4
2.3 | - Do - 3.5 x 16 sqmm with 02 nos 8 SWG bear GI.wire as running earth. for Light D.B | Mts | 10 | 250 | 2500 | 20
2.4 | - Do - 3.5 x 25 sqmmth with 02 nos 8 SWG bear GI.wire as running earth. for POWER & A.C D.B , UPS & ATM | Mts | 10 | 300 | 3000 | 16
2.5 | - Do - termination of 25 & 16 Sqmm 3.5 Core | Nos | 8 | 150 | 1200 | 8
3 | Out door type glow sign board wiring :-
3.1 | Supply laying of main line with 2x2.5 +1x1.5 mmsq through MS conduite from main panal to glow sign board. | Mts | 25 | 100 | 2500 | 25
3.2 | Supply installation of 16 amps DP MCB at main entrance Glow sign board & With Electronic timer as required. | Set | 1 | 1500 | 1500 | 1
4 | EARTHING STATION :
(i) | Earthing installation as per I.E. rule conforming | Set | 2 | 6000 | 12000 | 2
Supply, Installation, Testing and Commissioning of Maintenance Free Earthing system made up of copperbonded rod of 10 feet length,23 mm dia. (Minimum copper bonding shall be 0.25mm) along with Rod-toConductor connectors, Earth enhancement material, Pit Cover and other accessories as required and as per specification and other applicable codes (include chamber for earthing, Earthing certificate to be submitted along with the bill).
(ii) | Supply laying 2x8SWG copper bear wire from earth spike to main panal.(Electrolite wire)
|  | Mts | 20 | 150 | 3000 | 35
5 | MAIN ELECTRICAL DISTRIBUTION
5.1 | Main Panel (wall Mounted Type)
Supply, fabricating,assembling,internal- connection, testing & connceting with incomming, out going power cables & lines as required to complete the job of cubical type electrical panal made from 14SWG CRC. M.S. sheet with proper earthing terminal(Nut- bolt &washer) 02 No.outside of panal, same nut- bolt to tighten with internal earth busbar of panal situated inside loose wire box(on top portion of panel) On top side of panel cable entry arragement to be done for incomming & out going of lines. Painting powder coating electrical grey/ seimensgrey to be done.one 6"x4" enamal type 440Volt Danger board to fix up on main panal bus-bar cover, components are as follows :-All switches are front handle operated & all MCB knob should be visual, all component to provide in separate compartment only DBs in one compartment.
Incomer - 100A 4P MCCB 25Ka with adjustable thermal & Magnetic trip unit -1 Nos
OUTGOINGS -
63 Amps 4 pole MCB. = 04 Nos.(AC & Power DB,ATM ,UPS,spare ) 40 Amp 4 Pole MCB :2 nos (Lighting DB,Spare) 25 Amps DP MCB = 02 Nos.( sign board , Fire Alarm) Amps Meter 0-100 Amps with 3 Nos. CT & selector switch 96x96mm 01 Set (Changeover should be ON-LOAD type.)
100Amps 4pole Cu. Bus Bar. 01 Set. 100Amps 4 pole Change over switch. 01 No. 100 Amps FP MCCB 25KA as Gen - Set main incoming 01 NO.
Volt meter 0-500volt A.C. 50 Hz.96x96mm with selector switch. AE make.n 01 Set
20mmdia LED indicator lamp 03 Nos.
02 Amps Sliding Fuse. 06 Set.
150x100mm enamal Danger board 440 volt.
(to set on bus bar cover). 01 No.
| Cable entry from top & bottom - removable gland plates (bottom at 2 points) c/w powder coated Grey paint (two coats) with name labels for all incoming & outgoing feeders. The panel shall be complete in all respects including all accessories such as earthing bus, Air ventilators, lifting hooks etc. | Set | 1 | 25000 | 25000 | 1
5.3 | POWER DB & AC DB. Make standard/Legrand/ABB ,Double door
6 way TPN MCB DB with TP MCB as incoming
63 TP&N MCB as main
16Amps SP MCB - 8 Nos ( Ac :3 Nos + 2X6amp : 4Nos and 1Nos spare ) +32AMPS SP X10 NOS. (Ac 3 Nos+15 Amp: 6 Nos, 1No Spare)
| including Neutral Bar. 01 Set | Set | 1 | 3500 | 3500 | 1
5.4 | LIGHTING DB Make standard/Legrand/ABB
6 way TPN MCB DB with TP MCB as incoming
63A TP&N MCB as main
32 AMPS DB MCB 1No: For Strong room )
16 Amps SP MCB - 03 Nos.+ (BM +Toilet) each 1No + 1No spare
12 Amps SP MCB - 12 Nos. (Hall - 4Nos + Store room 1 No +Exteranl Lighting 1No.:+ Ups 1No + wall Fan 3 Nos.2 No spare)
| Including Neutral Bar. 01 Set | Set | 1 | 3500 | 3500 | 1
6 | UPS SYSTEM (Branch)
6.1 | UPS Main DB Supply, erection, testing and commissioning of three phase 4 WAY, TPN MCB DB double door type with "C" Curve MCBs, IP 42 powder coated for UPS with 63A 4P MCBs – 1No as INCOMER 32A TP MCBs – 3 Nos. as OUTGOING (UPS :2Nos and 1 set ,: Spare Including all interconnections & accessories etc Make standard/Legrand/ABB | Nos | 1 | 3500 | 3500 | 1
6.2 | Supply & Fixing of 32A DP MCB in 2way SPN Db IP 20 metallic directly on wall Raw power Incoming & OutGoing supply for UPS (Branch :2 Nos & ATM 1No.) | Nos | 3 | 1500 | 4500 | 2
6.3 | UPS DB-1 & 2 combined
| 12 Way SPN MCB DB with 'C" curve MCBs. Incoming : 2 No. 40A DP MCB Outgoing : 8 Nos 6/10A ( BM: 1+1 Nos with lighting : Server & Data Rack (1+1) Nos:C.C 2Nos with lighting :counter :2 Nos) SPO MCBs Make standard/Legrand/ABB . Repective UPS lighting to be connected.(BM,C.C,Banking hall 2Nos) or as per SLD | Nos | 1 | 2800 | 2800 | 1
6.4 | Supply and installation of modular type 3 nos 6A multi pin sockets with 2 nos 6A one way switch with indicator housed in MS box to be fixed in partitions or concealed in wall. The box shall be painted with 2 coats of enamel paint over a coat of red oxide primer including making connections complete the rate inclusive of Supplying and running of 3 runs of 2.5 sq.mm UPS DB's to individual powerstation through .(looping 2 sets of 3X6 A socket outlet in one circuit / or as per SLD the following size of 660 volts grade, Finolex brand PVC insulated wire (For UPS point only).(For B.M,C.C,Sever each 2Nos.) +5 Nos for Counter+Rack 1Nos) | Nos | 10 | 1500 | 15000 | 7
6.5 | Supply & Laying of 4 runs of 6.0 Sqmm and 2 runs of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid / flexible metal conduit from MainUPS DB to auto phase shifter. | mtr | 10 | 210 | 2100 | 10
6.6 | Supply, installation, testing and commissioning of 40A rated 3 phase to single phase auto phase shifter for 3.0 KVA UPS (SLHD of Swift make) | Nos | 2 | 2000 | 4000 | 2
6.7 | Supply & Laying of 2 runs of 6.0 Sqmm and 1 run of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid PVC conduit from automatch phase shifter to UPS unit | mtr | 10 | 180 | 1800 | 10
6.8 | Supply and Installation of Moduler type 2 X 20A plug & socket housed in for UPS output control (Branch 2 Nos & ATM 1No.) | Nos | 3 | 900 | 2700 | 3
6.9 | Supply & Laying of 2 runs of 4.0 Sqmm and 1 run of 2.5 sqmm, PVC insulated, single core, multistranded copper conductor cable in suitable rigid / flexible metal conduitfrom 3 KVA UPS to UPS DB | mtr | 10 | 160 | 1600 | 10
| sub total I |  |  |  | 158750 |  |  | 0
8 | ELECTRICAL FITTINGS (S/I/T/C
8.1 | Supply and Installation Recess mounted 2'-0"X2'-0" watt ,38 W LED FULL GLOW Philips MAKE . Light should be fixed through SS threaded bolt tighted the upper end on ceiling using anchor bolt and lower end on Light fitting with nut and bolt (RC380B G2 LED35S-6500/4000 PSU OD WH)PHILIPS/WIPRO MAKE | Nos. | 14 | 3000 | 42000 | 9
8.3 | SQUARE SHAPE DOWNLIGHTER - INTEGRA 15W, 3000K, LHEBGTP5Z1W015, PHILIPS Razor/WIPRO MAKE | Nos. | 27 | 900 | 24300 | 22
8.4 | TUBELIGHT - TITANIA SLEEK NEW LED TUBELIGHT 36 W, LHLDCNVENL8Z018, PHILIPS/WIPRO MAKE. | Nos | 9 | 500 | 4500 | 7
8.5 | HANGING LIGHT - LHECDOL5PW1W040 (40WATTS), PHILIPS/WIPRO MAKE | NOS. | 2 | 400 | 800 | 1
8.6 | 150 mm dia Heavy Duty Exhust fan 230 voltA.C.( Havells / Crompton make).(UPS & Toilet ) | Nos | 3 | 1300 | 3900 | 2
8.7 | Wall mountaing fan 400 mm dia 230 volt A.C. PHILIPS/WIPRO MAKE | Nos. | 10 | 2000 | 20000 | 7
8.8 | Supply of Ceiling fan with 1200mm sweep, double ball bearing motor, capacitor, three MS blades die cast Al housing in stove enameled white with, suspension rod including all accessories of approved make.(5 star rated) (ORIENT/KHAITAN).(UPS,Strong room & Store room) | Nos. | 4 | 1800 | 7200 | 3
| SUB TOTAL |  |  |  | 102700 |  |  | 0
| TOTAL FOR ELECTRICAL WORK (B) |  |  |  | 261450 |  |  | 0
C | SCHEDULE - 'C' (LAN & TELEPHONE WORK )
S.NO. | DESCRIPTION | UNIT | QTY. | RATE | AMOUNT | QTY. | RATE | AMOUNT
2 | DATA SYSTEM - CONDUITING & CABLING
2.2 | Wiring for computer networking from I/O hub to computer workstation with UTP Cat-6 computer cable including providing ferrules at both ends and termination at both ends including providing & fixing frame for with shutter, RJ 45 outlet, faceplate and mounting box complete of modular type, This work includes providing PVC conduits ( 1/2", 3/4" size or as required0 in chases from the I/O hub to the point. The cost includes testing, commisioning etc complete. Note : Do not run more than 3 wire in single pipe & should be concealed. ( Server,BM,CC & ATM each 2Nos and counter 5Nos) | Nos. | 9 | 1200 | 10800 | 7
2.3 | Supply of Cat - 6 D-Link patch cord 7' 0" (ATM 1No) | Nos. | 9 | 200 | 1800 | 7
2.4 | Supply of Cat - 6 D-Link patch cord 3' 0"(ATM 2No) | Nos. | 9 | 150 | 1350 | 7
2.5 | Supply & fixing 24 Port Jack Panel Make:-D-Link | Nos. | 1 | 4500 | 4500 | 1
2.6 | 19" Rack 9U with Glass Door , Locking system Make: APW | Nos. | 1 | 4500 | 4500 | 1
2.7 | 24PORT 10/100Mbps Switch | Nos. | 1 | 4500 | 4500 | 1
| GRAND TOTAL FOR LAN & TELEPHONE (C) |  |  |  | 27450 |  |  | 0
D- AIR CONDITIONING WORK
S.NO. | DESCRIPTION | UNIT | QTY. | RATE | AMT | QTY. | RATE | AMT
(AIR CONDITIONING WORK)
C | 3-Star rated Hi-wall split airconditioner of 1.0 TR capacity | Each | 0 | 29500 | 0
2 | Additional copper piping for instalation of split 1.0/ 1.5/ 2.0 TON Ac's at far end with wiring & drain pipe. | Rmt | 40 | 600 | 24000 | 40
| TOTAL |  |  |  | 24000 |  |  | 0
| GRAND TOTAL-B+C+D |  |  |  | 312900 |  |  | 0
NOTE :- GST TAX WILL BE EXTRA.
Mohit & Associates. Architects,Interiors .Estimators L-2/554-, Vineet Khand, Gomti Nagar,Lucknow. Phone.742821765,9582218092 E-Mail: mohitg.gupta2783@gmail.com

## ATM (hidden)
ESTIMATE INTERIOR WORK FOR INDIAN BANK AT SEVLA AGAR E-LOBBY.
SCHEDULE - 'A' ( FURNISHINGS WORKS )
SN | Item description | Unit | Quntity | Rate (Rs.) | Amount
1.1 | Wall Paneling
Providing & fixing in position column cladding consisting of 6mm
thk comm. ply and 2" X 1" wooden section finished with 1.0 mm
laminate to the column /wall after grouting & screwing. After
wooden panelling , the rest of the column is to be texture/ heritage
painted.The item is to be completed in all respects as per
| design,direction & approval of the architect. | Sq.Ft. | 200 | 150 | 30000
1.2 | MAIN Entrance Glazing with door
| work will be complete incuding 6"x1.75" bottom and 5"x1.75" toprail wooden steam beach section duly melamine finish, 10mm Thk. Toughened Glass, heavy duty door spring ,SS finish handle,lock godrej make. | SFT | 100 | 250 | 25000
1.3 | Granite Cladding(ELEVATION).
| Providing and fixing granite slabs size of 2'x1' fixed with adhesive finish with jointing compound edges to be moulded polished all complite as per direction and approval of the Architect. | Sq.Ft. | 0 | 345 | 0
1.4 | STORAGE
Providing and fixing Full height storage 750mm deep made out of 19mm bwp block board finished with 1.0mm laminate in all exposed areas . The drawers to be made out of 19mm BWP block board in the front cladded with 1.0mm laminate( color, vertical grain) .sides to be made out of 12mm plywood and bottom made out of 6mm plywood duly painted in matching tone and it should play on drawer sliding channels . The shutters to be made out of 19mm block board and should play on drawer sliding castors on powder coated channels. The necessary locks , handles, etc to be provided . 3" x1/2 wooden skiritng to be provided duly polished as per matching tone all along the visible areas . Inside of the unit to be enamel painted in matching tone . All the exposed edeges of the boards/plywoods to be coverd with wooden lippings/mouldings duly polished all complete.The work to be completed as per approval and specificaion of the Architect.
| Full/Low ht storage | Sq.Ft. | 30 | 500 | 15000
1.5 | OUTER SHUTTTER BOX
| Overhead outside shutter box: p/f sal /maranti wood frame fixing of 12mm plywood with 1mm thk. Laminate finish and openable shutter for out side area | Sq.Ft. | 40 | 150 | 6000
1.6 | STAIRCASE IN MS ANGLE FRAME / PIPES AND SUPPORTED WITH PIPES - (Area of steps and landing only will be measured.) | Sq.Ft | 0 | 525 | 0
Providing and fixing Staircase in Steel structure as per design using channel and angles for steps & supported in C channels / I sections. The whole structure has to be supported with MS Angle/ I section on respective points grouted to the floor using MS Plates as per design complete with 2 coats of primer.
| SUB TOTAL |  |  |  | 76000
ELECTRICAL WORK
2.1 | Supply,laying, connection &testing of light,
fan point, wiring by 2x1.5mmsq(2x3/.029) +
1x1mmsq PVC insulated copper flexiable wire
maintating the colour code as per direction in
PVC conduite of 20mm with ISI mark 1.5mm
thickness to conceal in wall partition mending
good the damage, complete with PVC circular
box, bend to be done as per drawaing
including 3 point ceiling rows wherever
required GI saddle to be used for fixing,
metal flexiable/PVC flexiable pipe may use
if requied in partition wall. All PVC pipes
should be with ISI mark. No joints will be
allowed inside pipe ,light, fan & plug point
complete with modular type switch plate &
MS box .
Lighting point complete with modular type
switch, plate, M.S. conceal box.
A | Point - 1 Light point control by 01 switch. | Nos | 2 | 550 | 1100
B | Point - 2 Light point control by 01 switch. | Nos | 3 | 650 | 1950
2.2 | Wall bracket fan point as above complete with modular type switch,plate & M.S. conceal box. Including one 2pin plug socket,front plate & conceal box at fan end. | Nos | 2 | 700 | 1400
2.3 | Supply Laying of Circuit line2x2.5mmsq +1x1mmsq PVC insulated copper wire form MCB DB(LDB) to lighting SB & Raw power plug point (6Amps)rest are same as item no.1.3 light board or 6 amps plug connected from one circuite. | Mts | 20 | 95 | 1900
2.4 | Supply Fixing & connection of modular type 6 amps Plug switch complete with Ms box Socket to fixed above table. 03 nos plug can be connected from 01 circuite | No. | 4 | 650 | 2600
2.5 | Same as above but 16 Amps 6pin socket with 16amps switch for raw power point. ( 01 Nos plug connected from one circuite.) including wire 2x4 +1.5sqmm earth wire. | No. | 4 | 1150 | 4600
2.6 | TELEPHONE WIRING.
| Supply laying & connection of same as item no.1 but with 2 pair 0.5 sqmm tinned CU conductor through PVC regid ISI mark pipe from telephone point to Korne DB complete with RJ - 11 telephone socket modular type in MS conceal box. | No. | 2 | 550 | 1100
2.7 | Same as above 20 pair 0.5 sqmm copper conductor telephone cable in 20mm dia PVC pipe. | Mts | 10 | 85 | 850
PARTICULAR
SUPPLY FIXING & CONNECTION
LIGHT FITTINGS / FANS :
2.8 | Wipro make Recess mounted 2x36watt CFL WIPRO MAKE FITTING 2'-0"X2'-0"(WVP- 25236) | Nos. | 2 | 3000 | 6000
2.9 | Wipro make 1x40 watt Tubelight fittingswith truelite with both end cap white | Nos. | 0 | 675 | 0
2.1 | Wipro make Recess mounted 2x18watt CFL WIPRO MAKE FITTING WCP- 32218) | Nos | 6 | 1100 | 6600
2.11 | Wall mountaing fan 400 mm dia 230 volt A.C. | Nos. | 2 | 1500 | 3000
2.12 | UPS WIRING :
| Supply fixing & connection of UPS circuite line with 2x2.5+1x1.5mmsq through regid PVC conduite 20mmdia 1.6 mm wall tickness, with ISI mark, to lay from UPS MCB DB to plug point board.rest same as item no.1 Two nos point to be connected from One circuite . | Mts | 15 | 105 | 1575
2.13 | Suppy fixing of 2x6Amps 5 pin socket + 1x16 Amps 6 pin socket in single board (under table) + 1x16 A switch in another board above table as per direction. | Set | 4 | 550 | 2200
2.14 | Same as above but 3x6/16, 6pin socket with switch to provide near HUB rack, are to be connected from UPS power. | Set | 0 | 800 | 0
2.15 | Supply laying & connection of UPS incomming power linewith 2x6mmsq +1x2.5 PVC insulated copper wire rest same as item no item no. 1 from PDB to UPS incomming power switch.including 1 nos outgoing line. | mtr | 0 | 158 | 0
2.16 | Supply installation of UPS incomming 63Amps DP MCB with orginal housing of Legrand make. | no | 0 | 800 | 0
2.17 | Supply installation and termination of UPS outgoing power distribution system with8+2Way SPN DB comprising8x10Amps SP MCB & 40 Amps DP MCB as main | no | 0 | 2200 | 0
2.18 | LAYING OF CABLE :
a) | Supply laying fixing main power with 50 mm sq 3.5 core PVC insulated,PVC sheated Alu.Conductor, 1100 v. grade armoured cable complete with 02 nos 8 SWG bear GI.wire as running earth. | Mts. | 0 | 375 | 0
b) | End termination of 50 mmsq 3.5 Core armoured cable,complete with brass cable gland , Alu. Lug, PVC tape. | End | 0 | 220 | 0
2.19 | Supplying & laying of following1100 V grade XLPE insulated & FRLS PVC sheathed armoured aluminium conductor cables conforming to IS 7098 with 2x 8 SWG G.I Wires by GI bar and saddles on wall/ ceiling and wall/floor pass through GI class B GI pipe.
a | 4x 25 Sq mm For Power D.B + AC D.B | Metre | 20 | 260 | 5200
b | 4x 10 Sq mm For ligh tD.B. | Metre | 15 | 220 | 3300
2.2 | MAIN DISTRIBUTION BOARD
A | 4way TPN MCB DB with
63 TP&N MCB as main
16Amps SP MCB - 6 Nos+20AMPS SP X6 NOS.
| including Neutral Bar. 01 Set | Set | 1 | 5500 | 5500
2.21 | EARTHING STATION :
b) | SpikeEarthing with G.I. Electode 3mts. Longx50
mm dia (Class - B) including accessories and
providing masonary enclosure with cover
300x300mm plate having locking arrangement
and watering funnel Etc. with charcoal,
sand & salt at alternate layer as required
for electrical panal earthing.
| (For main electrical panel earthing.) | No. | 1 | 5000 | 5000
c) | Supply laying 2x8SWG copper bear wire from
| earth spike to main panal.(Electrolite wire) | Mts | 20 | 80 | 1600
d) | Do but with 1x16mmsq insulated
copper wire from earth spike to UPS earth
| bus bar through PVC regid 20mmdia ISI | Mts | 20 | 100 | 2000
mark.
2.22 | A/C. electrification :-
a) | Supply laying & connection of A/C. line for
| 2 /1.5TR A/C. window / splite with 2x4 + 1x2.5 | Mts | 20 | 125 | 2500
mmsq throughRegid PVC conduite rest same
item no 1.
b) | S/Fixing AC Box as per company specification with 25 Amp SPMCB with 25AMP Socket | Nos | 2 | 950 | 1900
2.23 | Out door type glow sgn board wiring :-
a) | Supply laying of main line with 2x2.5 +1x1.5 | Mts | 0 | 95 | 0
mmsq through MS conduite from main panal
to glow sign board.
b) | Supply installation of 16 amps DP MCB at main
| entrance Glow sign board WITH TIMMER MDS MAKE | Set | 0 | 3500 | 0
2.24 | Supply fixing of 100Amps TPN HRC type SFU
| at SEB for main incomming on MS angle. | No. | 0 | 4000 | 0
frame & 02 nos Cable end box including
connection.
2.25 | Gen set wiring :-
a) | Supply laying fixing main power with 3.5 core
50Sq.mm PVC insulated,PVC sheathed Alu.
| Conductor, 1100 v. grade armoured cable | Mts | 15 | 375 | 5625
complete with 02 nos 8 SWG bear GI.wire
as running earth.
b) | End termination of 3.5 core 50 Sq.mm | End | 0 | 220 | 0
armoured cable,complete with brass cable
gland , Alu. Lug, PVC tape.
| SUB TOTAL |  |  |  | 67500
| GRAND TOTAL FOR FURNISHING WORK |  |  |  | 143500
B | SCHEDULE - 'B' ( AC WORKS )
S.No | Item description | Unit | Quntity | Rate (Rs.) | Amount
AC WORK
3.1 | Air cooled Hi Wall Split AC Units Comprising Of:
Supply of aircooled split AC complete with indoor & outdoor
unit with cordless remote control as required
(I) | Nominal Capacity - 2.0 TR (Make - Blue Star,Hitachi , Voltas). | NO | 0 | 39000 | 0
(II) | Nominal Capacity - 1.5 TR ( Make - Blue Star,Hitachi , Voltas). | NO | 0 | 33000 | 0
(III) | Nominal Capacity- 1.0 TR ( Make - Blue Star,Hitachi , Voltas). | NO | 2 | 29000 | 58000
Note :- Rate including copper wire free 5 rmt.
3.2 | Installation testing comisioning of Hi -Wall Split AC
(I) | 2.0 TR Capacity | NO | 0 | 2400 | 0
(II) | 1.5 TR Capacity | NO | 0 | 2400 | 0
(III) | 1.0 TR Capacity | NO | 2 | 2400 | 4800
3.3 | Supply installation testing & comisioning of
Voltage Stabilizer of approved make
(I) | 4 KVA | NO | 2 | 2800 | 5600
Note: All voltage stabilizer is sufficient for
A.C.should have time delay facility.
3.4 | Copper Refrigerant Piping :
| Installation & commissioning of Soft copper piping with | RMT | 20 | 650 | 13000
complete fiting & insulation
3.5 | Drain Piping | .
| Hard PVC insulated drain water piping wprk of size 25 mm | RMT | 20 | 110 | 2200
dia with complete fiting Etc.
3.6 | Electrical Cable
Providing & fixing of interconected electrical wiring between
indoor & outdoor unit as req. complete as per design &
| specification of manufacturer. | RMT | 40 | 95 | 3800
3.7 | Frame Work
Supply fabrication & installation of MS
angle iron stand with safety cage for ODU
complete with hanger& suporting Arrange-
| ments as required. | NO | 2 | 4000 | 8000
3.8 | Civil Work For cutting Chisling Plastering of
walls to conseal copper pipe, Drain pipe &
| Electrical wire with plaster finish. | LS | 1 | 3000 | 3000
3.9 | Electrical wire with plaster finish.
| Providing and fixing timer switch for switching power alternatively between two A/C, timer will be analogue dial type adjustable TIMER switch which is adjustable over 24hrs. With 15 minutes intervals and is to have 1NO+1NC (20A) contact. Timer will have its own backup battery and will be enclosed in 16gauge MS Box with acrylic lid together with suitable connector block. (ABB/MDS/L&T) | NOS | 1 | 4000 | 4000
| GRAND TOTAL FOR AC WORK |  |  |  | 102400
C | SCHEDULE - 'C' ( RESIDUAL EXPENDITURE )
SN | Item description | Unit | Quntity | Rate (Rs.) | Amount
4.1 | FALSE CEILING
| Providing and fixing Gypsum false ceiling as per India Gypsum specification for ceiling with drops as per drawing including of providing and fixing G.I. Frame work as per specification of India gypsum at a distance of 2'0" c/c both ways complete with 12.5mm board and all necessary perimeter channels etc. Along with light and A/C vent cutting and finishing | Sft | 180 | 65 | 11700
4.2 | PAINTING AND FINISHINGS JOB
| Providing and applying Acrylic emulsion paints after removing the damaged plaster , replastering with 12mm thk cement morter finished with P.O.P to make the necessary smoothnes , reparingall damages . Then two coats of Primer of approved make to be applied finished with two or more coats of acrylic emulsion paints .The work to be completed as per approval and satisfaction of the Architect. | Sft. | 200 | 12 | 2400
1.3 | TEXTURE PAINT
| Providing and doing textured surface coating on wall of approved shade & texture besic rate Rs.45/sft. (Heritage flakes) the rate are inclusive of scaffolding staging etc. for any hight and for plane as well asfor architectural surface. All completes as per approval and instructions ofthe architect / employer. | SFT | 100 | 50 | 5000
4.3 | Dust bin
| Suppling a metal dust bin. | No | 1 | 1000 | 1000
4.4 | Door Mat | No | 1 | 1000 | 1000
4.5 | writing ledge
| Providing and fixing writing ledge as per design made out 19mm comm. board with necessary grove patterns with 1.0mm laminate. 10mm thk machine polished glass to be provided on top of the writing ledge. Small boxes to be made out of 12mm comm. ply to be made on top of the writing ledge finished with 1.0 mm laminate, inside enamel painted .The work to be completed as per design and approval of the architect. | no | 1 | 3000 | 3000
4.6 | 12mm Toughened Glass Partition ( E-Lobby ) | SFT | 75 | 375 | 28125
| GRAND TOTAL FOR CIVIL WORK |  |  |  | 52225
| GRANT TOTAL ( SCHEDULE - ' A+B+C ' ) |  |  |  | 298125